# Structured Plan Update: MORL/PPO-Centered Q1 Roadmap

# 1. Central Research Axis

Main claim: a calibrated digital twin is the enabling layer for reliable transfer and evaluation of downstream HVAC control policies, with MORL/PPO as the target controller family.

- Surrogate fidelity and inverse calibration are the foundation, not side branches.

- Thermostatic PPO and HDRL are supporting baselines and ablation anchors.

- MORL/PPO is the central destination, but it is not yet the strongest validated result.

# 2. Current Verified Status

## 2.1 Surrogate Fidelity Block - implemented

Evidence: results/research_benchmark/tables/surrogate_rollout_benchmark.csv and inverse_calibration_benchmark.csv

raw_v35: one-step RMSE 0.6135 C, 4h 0.7627 C, 8h 0.7659 C, 24h 0.7613 C, bias +0.0087 C, power RMSE 72.23 W, C_zon error 3.07%.

calibrated_v35: one-step RMSE 0.6161 C, 4h 0.7661 C, 8h 0.7695 C, 24h 0.7656 C, bias -0.0659 C, power RMSE 72.23 W, C_zon error 3.07%.

v35_heads_only inverse calibration: baseline RMSE 0.5338 C -> calibrated RMSE 0.5256 C, improvement 1.52%, C_zon error 3.07%.

Interpretation: Stage A/B/C already solves physical identification much better than rollout-drift correction. The calibrated twin is physically stronger, but not yet better on free-run rollout realism.

## 2.2 Main Controller Benchmark - partial

Evidence: outputs/bestest_air_article7_style_15min/summary.csv and results/research_benchmark/tables/controller_benchmark.csv

15 min heating-window results on bestest_air:

Thermostatic PPO, peak_heat_window: m_s 0.0725, violation 1.49%, rmse_22 0.8691 C, mean_power 958.9 W.

Thermostatic PPO, typical_heat_window: m_s 0.0947, violation 4.39%, rmse_22 0.6222 C, mean_power 1096.1 W.

HDRL, peak_heat_window: m_s 0.1466, violation 7.22%, rmse_22 1.2407 C, mean_power 864.8 W.

HDRL, typical_heat_window: m_s 0.2301, violation 7.14%, rmse_22 1.0003 C, mean_power 1035.9 W.

Interpretation: Thermostatic PPO is the current strongest validated comfort controller. HDRL is structured and energy-aware, but currently worse than Thermostatic PPO on heating m_s.

Missing piece: one canonical 15 min table with PI + Thermostatic + HDRL + MORL under the exact same protocol.

## 2.3 Predictive-Information Ablation - partial

M.2 proxy exists, M.3 GRU path exists, and M.1 infrastructure now exists. The final benchmarked M.1 vs M.2 vs M.3 comparison table is still missing.

## 2.4 Transfer Block - partial, now unblocked

The v35_calibrated direct-TSup adapter is already wired into MORL, Thermostatic, HDRL, and evaluation paths.

The currently running command training/train_thermostatic.py --surrogate-kind v35_calibrated belongs exactly to this downstream-control-alignment step.

## 2.5 Time-Step Ablation - partial

Both 1h and 15 min result families already exist, but there is still no single aligned 1h vs 15 min comparison table for the same controller family.

# 3. Match Against the Original Plan

The original plan was directionally correct, but it needed three corrections:

1. MORL/PPO must be the central target, not an optional branch.

2. Each experimental block must be tagged as implemented, partial, or experimental.

3. The calibrated twin must be described honestly: it improves physical identifiability, not yet free-run rollout realism.

# 4. Immediate Next Steps

1. Finish the current Thermostatic PPO run on v35_calibrated.

2. Retrain HDRL on v35_calibrated.

3. Run MORL surrogate pretraining on v35_calibrated, then fine-tune and evaluate on BOPTEST.

4. Produce one canonical 15 min controller benchmark table with PI, Thermostatic, HDRL, and MORL on peak_heat_window and typical_heat_window.

5. Finalize the predictive-information ablation M.1 / M.2 / M.3.

6. Add one transfer table: trained on surrogate -> fine-tuned on BOPTEST -> evaluated on BOPTEST.

7. Keep the inverse problem frozen at v3.5 heads_only unless a rollout-aware calibration clearly improves 24h free-run metrics.

# 5. Writing Constraints for the Q1 Paper

- Do not claim that calibrated v3.5 already improves rollout realism.

- Do not present MORL/PPO as the strongest result yet.

- Use Thermostatic PPO as the current strongest validated heating controller.

- Use the calibrated twin as the methodological bridge that makes the future MORL transfer story credible.

# 6. Updated Core Hypothesis

A calibrated digital twin with explicitly identified building physics enables more reliable controller transfer and makes multi-objective HVAC control evaluation reproducible, comparable, and scientifically defensible in BOPTEST.